## BoQ
PROPOSED USHURU PENSION TOWERS FIRE ESCAPES
ELECTRICAL INSTALLATIONS
ELECTRICAL BILLS OF QUANTITIES
ITEM | DESCRIPTION | UNIT | QTY | RATE, KSHS. | AMOUNT, KSHS.
A | GENERAL ITEMS AND ATTENDANCE
A/1 | Inspect proposed electrical layouts and existing electrical installations, existing electrical riser ducts, existing cable pathways and cabling and allow to alter, adjust, clear, extend cableways and cabling | Item | 1 |  | 0
A/2 | Allow for the preparation of all detailed working design drawings, fully cordinated with other services (Allow set of 12 A1 drawings). | Sets | 3 |  | 0
A/2 | Allow for the preparation of all detailed "As built" design drawings, fully cordinated with other services inclusive of delivery of soft copies to clients (Allow set of 12 A1 drawings). | Sets | 3 |  | 0
A/3 | Allow for TRAINING of Client's O & M Personnel on the operation and Maintenance of specialist electrical equipment supplied under this contract | Sum | 1 |  | 0
A/4 | The Tenderer is to describe hereunder inserting any relevant clause number, any other works, obligations or items that may be referred to in the Conditions of Contract, Specification, Drawings or Data Schedule in respect of the works for which he desires to enter a separate charge( this charge is to be entered in the Amount column). If no charge is entered hereunder, rates and amounts elsewhere in the schedule of prices shall be deemed to cover all expenses for such works, obligations or items including all PRELIMINARIES | Sum | 1 |  | 0
A/5 | Allow for the removal and handing over to the Client of existing Electrical installations during demolishion works. | Sum | 1 |  | 0
A | SUB-TOTAL CARRIED FORWARD TO SUMMARY PAGE |  |  |  | 0
B | ELECTRICAL DISTRIBUTION
B/1 | Allow for ispection of the existing sub-boards, expansion of the LV board, installation of additional busbars, extension panels, 2 Nos. 160A TP MCCBs outgoers as necessary to allow for connection of new 2No. DBs with matching MCCBs and the necessary accessories (Note that the expansion works should be done by a specialist switchboard manufacturer) | Sum | 1 |  | 0
B/2 | Supply and install complete all earthing requirements for the main switchboard under item B/1 including concrete inspection pits, rods, tapes etc. all as per the requirements of the technical specifications | Sum | 2 |  | 0
B/3 | Supply, install and connect 9 way SP/N surface mounted distribution boards for Raw power as Schneider or approved equivalent complete with 100A DP incomer and 9 Nos. 16A/10A/6A 10KA SP MCB units as per schematic wiring diagram | No | 6 |  | 0
B/4 | Allow for all Labeling all distribution boards, and sub- as per technical specifications | No. | 6 |  | 0
B/5 | Allow for the Bonding of the Consumer units under item above including concrete inspection pits, rods, tapes etc. all as per the requirements of the technical specifications | Sum | 6 |  | 0
B/6 | Supply, install and connect 10.0 mm² x 3 core PVC SWA PVC cable from the building distribution boards, Consumer Units above | m | 320 |  | 0
B/7 | Supply, install and connect 10.0 mm² PVC insulated single core earth cable for above power cable. | m | 350 |  | 0
B/8 | Terminations for above 10.0 mm² x 1 core PVC cable inclusive of glands and lugs | No. | 6 |  | 0
B/9 | 100mm x 50mm x16 SWG galvanized sheet metal cable tray on support brackets raw bolted under side of floor slab/ installed in electrical riser ducts complete with bends and tees and any other accessories to complete the installations all installed to latter instructions on site. | m | 260 |  | 0
B/10 | Supply, install and connect 63 Amp TP/N isolator for Mechanical equipment power supply as specified and detailed on the drawings | No. | 6 |  | 0
| SUB TOTAL CARRIED FORWARD TO THE NEXT PAGE |  |  |  | 0
| SUB TOTAL BROUGHT FORWARD FROM THE PREVIOUS PAGE |  |  |  | 0
B/11 | Supply, install and connect 16.0 mm² x 4 core PVC SWA PVC cable from the building distribution boards, to Isolator above. | m | 128 |  | 0
B/12 | Supply, install and connect 20 Amp SP/N isolator for Mechanical equipment power supply as specified and detailed on the drawings | No. | 3 |  | 0
B/13 | Supply, install and connect 6.0 mm² x 3 core PVC SWA PVC cable from the building distribution boards, to Isolator above. | m | 180 |  | 0
B | SUB-TOTAL CARRIED FORWARD TO SUMMARY PAGE |  |  |  | 0
C | ELECTRICAL INSTALLATION
C/1 | Supply only complete the following light fittings including bulbs and tubes, and fixings:
| b) Type D - 1x13 watts, 135mm diameter, recessed TC-DEL lamp downlighter with integral high frequency control gear, halo attachment, specular anodised aluminium reflector as Thorn Chalice 135 | No. | 50 |  | 0
| b) Type LED - 65 watts, 600mm square light, warm white, medium beam finished in aluminium as Philips or equal approved. | No. | 50 |  | 0
| c) Type EXIT: Ultra slim maintained LED exit sign with doubled sided sign blades as Thorn Voyager LED. | No. | 15 |  | 0
C/2 | Take delivery and install complete the following light fittings including bulbs and tubes, testing and commissioning
| c) Type D | No. | 50 |  | 0
| d) Type LED - | No. | 50 |  | 0
| b) Type EXIT - | No. | 15 |  | 0
C/3 | Supply, install and connect new lighting points/ extensions to existing points complete with 3x1.5 sq mm single core cables, .5 sq. mm 3 Core flex cables concealed in conduit/ installed within gypsum ceiling, complete with draw boxes, connectors, switch boxes and other necessary accessories. | No. | 115 |  | 0
C/4 | Supply, install and connect - concealed fixing lighting switches finished in satin steel as Hamilton "Linea-Duo" range complete with associated concealed conduits
| (c) 1 gang intermediate switch | No | 25 |  | 0
| (d) 2 gang 2 way | No | 10 |  | 0
C/5 | Supply, install and connect - 13 Amp twin socket outlets points on wall/ trunking/ floor box complete with conduit, ring main wiring in 3x2.5 sq. mm SC PVC cables and all accessories necessary for flush mounting | No. | 5 |  | 0
| SUB TOTAL CARRIED FORWARD TO THE NEXT PAGE |  |  |  | 0
| SUB TOTAL BROUGHT FORWARD FROM THE PREVIOUS PAGE |  |  |  | 0
C/6 | Supply, install and connect 13 Amps twin socket outlets finished in satin steel as MK or equivalent approved for normal power. | No. | 5 |  | 0
C/7 | Supply, install and connect CCTV, PIR sensor, vibration sensor, security outlet point consisting of average 15 meters of 20 mm diameter concealed heavy gauge PVC conduit inclusive of conduit, couplers, draw boxes, switch boxes, draw wire and other necessary accessories and white blanking cover to security alarm specialists requirements. (Provisional). | No. | 30 |  | 0
C/8 | Supply and install 240V/ 50Hz PIR motion sensors with dual element infra red sensor, rated at 1000 watts, with 360⁰ detection angle, adjustable delay time settings of upto 30 minutes and range of up to 8 meters (installed in areas agreed with engineer). | No. | 30 |  | 0
C/9 | Supply and install 20A four pole contactors in ventilated metal enclosures for above circuits. | No. | 5 |  | 0
C/10 | Allow for wiring to override backup switches in 3x1.5 sq mm PVC single core cables in concealed conduits. | No. | 5 |  | 0
C/11 | Supply and install override backup switches. | No. | 5 |  | 0
C/12 | Allow for load balancing, testing and commissioning of the entire electrical installation on this floor | Sum | 1 |  | 0
C | SUB-TOTAL CARRIED FORWARD TO SUMMARY PAGE |  |  |  | 0
D | FIRE DETECTION AND ALARM SYSTEM
D/1 | Supply and install complete 2 loop analogue addressable fire detection and alarm system as Menvier DF6000 or equivalent by HF Fire but approved by engineer complete with printer and other necessary accessories, as per the specifications | No. | 1 |  | 0
D/2 | Supply and install input output interface unit as Menvier MIO230 or similar but approved with mains rated contacts | No. | 1 |  | 0
D/3 | Supply and install additional manual call points unit to match existing complete with conduit and termination for wiring as shown on the drawings and as per approved working drawings. | No. | 30 |  | 0
D/4 | Supply and install additional Smoke Detector / Sensors unit to match the existing complete with conduit and termination for wiring a shown on the drawings and as per approved working drawings. | No. | 30 |  | 0
D/5 | Supply and install additional Heat Detector / Sensors unit to match the existing complete with conduit and termination for wiring as shown on the drawings and as per approved working drawings. | No. | 3 |  | 0
D/6 | Supply & install 150 mm dia. electronic bell to match the existing complete with cable termination. | No. | 30 |  | 0
D/7 | Allow for fire rated multicore cabling to the new accessories inclusive of alterations to existing cabling to match new layouts and any other accessories necessary for the complete wiring, testing and commissioning of the entire fire detection and alarm installations | Sum | 1 |  | 0
D/8 | Supply and install 20 Amp DP, switches, flush with neon indicators for Fire Detection and Alarm System power supply | No. | 1 |  | 0
D/9 | Allow for programming by the specialist supplier of the entire Fire Detection and Alarm System | Sum | 1 |  | 0
D/10 | Allow for fire man switch installation complete with conduits, couplers, boxes, cabling and push buttons. | Sum | 1 |  | 0
D/11 | Allow for TRAINING of Client personnel on the fire detection and alarm system operations | Sum | 1 |  | 0
D/12 | Allow for testing and commissioning of the fire detection and alarm system | Sum | 1 |  | 0
D | SUB-TOTAL CARRIED FORWARD TO SUMMARY PAGE |  |  |  | 0
H | LIGHTNING PROTECTION AND GROUNDING SYSTEM
H/1 | Supply and install 25 mm x 3 mm copper tape conductor complete with saddles and clamps etc. | m | 525 |  | 0
H/2 | Supply and install 1000 mm long taper pointed air terminal complete with terminal base and all necessary accessories | No | 12 |  | 0
H/3 | Ditto but multiple terminal point | No | 12 |  | 0
H/4 | Ditto but ridge saddle | No | 12 |  | 0
H/5 | Supply and install screw down test clamps and all necessary accessories | No | 15 |  | 0
H/6 | Supply and install 20 mm x 1200 mm long copper earth rod complete with spike, driving stud, dowel and clamps | No | 15 |  | 0
H/7 | Supply and install copper earth plates and mats (area as necessary) complete to all earth termination pits all to meet the requirements of the technical specifications | No | 20 |  | 0
H/8 | Supply and install concrete inspection pit complete with water proof cover for earth test/ rod inspections. | No | 15 |  | 0
H/9 | Allow for bonding the entire roofing structure to the lightening protection and grounding system | Sum | 1 |  | 0
H/10 | Allow for the supply, install, test and commission appropriate transient over voltage protection equipment on all power switchboards, telephone, data and structured cables entering or leaving the building, in order to protect equipment connected to power distribution system against transient over voltages coming into the building from outside all as per the requirements of the technical specifications | No. | 8 |  | 0
H/11 | Allow for testing and commissioning for entire lightning protection and grounding system | Sum | 1 |  | 0
0
SUB-TOTAL CARRIED FORWARD TO SUMMARY PAGE
I | IP CCTV INSTALLATIONS
I/1 | 3 MPx Enviromental Dome, Varifocal Lens with IR, Full HD, Digital WDR, Edge recording upto 64GB, IP66 Rated, PAL, IR Dome, True D/N, H.264, 3D DNR Digital Noise Reduction, PSIA/ONVIF/CGI, minimum 15m IR, 2.8 to 12mm @ F1.2, PoE / 12VDC - TVD-1104 | No | 39 |  | 0
I/2 | HD Netwok Video Recorder (NVR), 32 channel HD Network Video Recorder with minimum 8 TB internal storage, H.264 & MPEG-4 dual-streaming, 5 MPX resolution support, HD & Full HD real-time support, 160 Mbps for incoming streams, ezDDNS, HDMI, VGA and composite outputs - TVN-2132P-8T | No | 1 |  | 0
I/3 | Video Management Software for upto an unlimited number of clients connection, 75 Video Tiles using 3 Monitor views, Android & IOS phones & tablets support or equivalent approved | No | 1 |  | 0
I/4 | Remote CCTV System Monitoring Workstations complete with Surveillance System Software, OS and two (2) 24'' HD Monitors | No | 1 |  | 0
I/5 | Cisco WS-C2960X-24PS-L Catalyst Network Switch PoE Managed Switch or equivalent approved | No | 1 |  | 0
I/6 | 22U wall mounted rack cabinet - 900mm deep | No | 1 |  | 0
I/7 | Cabling, installation, termination, testing, commissioning & training | No | 1 |  | 0
I/8 | Allow for the integration of the CCTV system, to the access control system, intruder alarm system and fire alarm system for seamless operation. | No | 1 |  | 0
0
SUB-TOTAL CARRIED FORWARD TO SUMMARY PAGE

## MAIN SUMMARY
PROPOSED USHURU PENSION TOWERS FIRE ESCAPES
SUMMARY OF COSTS FOR ELECTRICAL INSTALLATIONS
ITEM | DESCRIPTION | AMOUNT
KSHS
SUMMARY PAGE FOR ELECTRICAL INSTALLATIONS
I | PRELIMINARIES
A | GENERAL ITEMS AND ATTENDANCE | 0
B | ELECTRICAL DISTRIBUTION | 0
C | ELECTRICAL INSTALLATION | 0
D | FIRE DETECTION AND ALARM SYSTEM | 0
E | LIGHTNING PROTECTION AND GROUNDING SYSTEM | 0
F | IP CCTV INSTALLATIONS | 0
G | Sub total for Electrical Installations | 0
I | SUB- TOTAL AMOUNT FOR ELECTRICAL INSTALLATIONS | 0
PC SUMS AND CONTINGENCIES
J | CONTIGIENCY | 500000
COST ESTIMATE FOR THE RECOMMENDED RENOVATIONS
K | OVERHAULING OF FIRE DETECTION SYSTEM | 1056000
L | REPAIRING OF FAULTY ELECTRICAL FITTINGS AND INSTALLATIONS | 3520000
M | INSTALLATION OF A FIREMAN’S SWITCH | 650000
N | INSTALLATION OF EMERGENCY LIGHTING | 2856400
O | SUB TOTAL OF ELECTRICAL INSTALLATIONS AND PC SUMS | 8582400
P | ADD 16% VAT | 1373184
Q | ADD 0.03% OF THE SUBTOTAL FOR CAPACITY BUILDING LEVY (EXCLUSIVE OF VAT) | 2574.72
R | TOTAL AMOUNT FOR ELECTRICAL INSTALLATIONS CARRIED TO FORM OF TENDER INCLUSIVE OF ALL APPLICABLE TAXES) | 9958158.72

## fifth floor (hidden)
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
|  |  |  | KSHS | KSHS
H | ELECTRICAL INSTALLATION - FIFTH FLOOR
`
H/1 | Supply only complete the following light fittings including bulbs and tubes, and fixings:
| a) Type F2: 1200mm loong, 1x28 watts T5 lamp high frequency gear fluorescent fitting as Thorn Micropak in kitchen | No. | 1 | 2500 | 2500
| b) Type A - 600x600mm 4x18 watts with mirror louvres and high frequency electronic gear | No. | 40 | 5000 | 200000
| c) Type C - 1x18 watts recessed PL downlighter in passages with facetted aluminium reflector as Philips Fugato | No. | 25 | 4500 | 112500
| d) Type F - 2x18 watts recessed PL downlighter in meeting rooms withhigh gloss mirror reflector as Philips Fugato compact FBS261 | No. | 2 | 5500 | 11000
| e) Type EXIT:¦ Ultra slim maintained LED exit sign with doubled sided sign blades as Thorn Voyeger LED. | No. | 2 | 18000 | 36000
| f) Type AE - as type A but with 3 hours emergency kit | No. | 5 | 13000 | 65000
| g) Type CE - as type C but with 3 hours emergency kit | No. | 3 | 12000 | 36000
H/2 | Allow for modification of lighting systems in the lift lobby to provide the following (provisional):
| a) Recessed circular LED downlghter to match existing ceiling cut-outs | No. | 6 | 11500 | 69000
| b) Recessed LED rope installed in ceiling coffer | LM | 14 | 3500 | 49000
H/3 | Take delivery and install complete the following light fittings including bulbs and tubes, testing and commissioning
| a) Type F2 | No. | 1 | 750 | 750
| b) Type A/ AE - | No. | 45 | 750 | 33750
| c) Type C/ CE - | No. | 28 | 750 | 21000
| d) Type F/ FE - | No. | 2 | 750 | 1500
| e) Type EXIT | No. | 2 | 750 | 1500
| SUB-TOTAL CARRIED FORWARD TO NEXT PAGE |  |  |  | 639500
| Brought Forward from previous page |  |  |  | 639500
H/4 | Supply, install and connect new lighting points/ extensions to existing points complete in 1.5 sq. mm 3 Core flex cables concealed within gypsum ceiling, complete with draw boxes, connectors, switch boxes and other necessary accessories. | No. | 78 | 1200 | 93600
0
H/5 | Supply, install and connect - lighting switches with associated concealed conduits |  |  | 0
0
| (a) 1 gang 1 way | No. | 15 | 350 | 5250
| (b) 1 gang 2 way | No. | 2 | 400 | 800
| (b) 2 gang 2 way | No. | 5 | 450 | 2250
| (b) 8 gang 2 way Grid switch | No. | 1 | 1800 | 1800
0
H/6 | Supply, install and connect - 13 Amp twin socket outlet point complete with conduit, ring main wiring in 3x4.0 sq. mm SC PVC cables and all accessories necessary for flush mounting | No. | 40 | 2200 | 88000
0
H/7 | Supply, install and connect - non standard13 Amp twin socket outlet (clean power) point complete with conduit, ring main wiring in 4.0 sq. mm SC PVC cables and all accessories necessary for flush mounting and complete with 3core 2.5mm sq flex termination below workstation top | No. | 70 | 2200 | 154000
0
H/8 | Supply and install 13A standard twin socket outlet for raw power as "MK" Logic or Crabtree | No. | 40 | 700 | 28000
0
H/9 | Supply and install 13A non-standard twin socket outlet for clean power as "MK" Logic or Crabtree | No. | 70 | 3000 | 210000
H/10 | Supply, install and connect 13 Amps non-standard fused plug tops complete with 1 m long 2.5 sq mm PVC PVC high temperaature cable for clean power socket outlets (provisional). | No. | 70 | 500 | 35000
H/11 | Supply only 13Amps 3pin standard fused socket plug-top | No. | 40 | 400 | 16000
0
H/12 | Allow for labelling UPS socket outlets with engraved plastic labels to approval | Sum | 70 | 150 | 10500
| SUB-TOTAL CARRIED FORWARD TO NEXT PAGE |  |  |  | 1284700
| Brought Forward |  |  |  | 1284700
H/13 | Ditto as above item above but 13Amp single socket outlet switched | No. | 2 | 600 | 1200
0
H/14 | Supply, install and connect 45Amps cooker control unit with neon light and 13A single switched socket outlet. | No. | 1 | 4000 | 4000
0
H/15 | Supply, install and connect - wiring to 45 Amp Cooker Unit outlet point complete with conduit, ring main wiring in 6.0 sq. mm SC PVC cables and all accessories necessary for flush mounting | No. | 1 | 4500 | 4500
H/16 | Supply, install and commission 250mm x 50mm x18 SWG powder coated 2 compartment sheet metal power cable trunking on support brackets raw bolted to wall complete with cover, bends and tees and any other accessories to complete the installations | No. | 70 | 2800 | 196000
0
H/17 | Supply, install and commission 100mm x 50mm x18 SWG powder coated 1 compartment sheet metal power cable trunking on support brackets raw bolted to ceiling soffit complete with cover, bends and tees and any other accessories to complete the installations (provisional, installed in ceiling space) | m | 50 | 1800 | 90000
0
H/18 | Provide 5x25mm HG PVC conduit links between the trunking and the distribution boards to approved working drawings | LM | 200 | 80 | 16000
0
H/19 | Provide 3x32mm HG PVC conduit links between the trunking and the distribution boards to approved working drawings | LM | 100 | 110 | 11000
0
H/20 | Allow for attendance during installation, testing and commissioning of A/C units by others | Sum | 1 | 10000 | 10000
0
H/21 | Supply and install 20 Amp DP outlets flush with neon indicators for A/C Units, hand drier and other general equipments | No. | 8 | 800 | 6400
0
| SUB-TOTAL CARRIED FORWARD TO NEXT PAGE |  |  |  | 1623800
| Brought Forward |  |  |  | 1623800
H/22 | Supply, install and connect complete 3 x 4.0 sq.mm cabling to 20 Amp DP outlet points for hand driers and various equipment (allow 30m radial circuits) | No. | 8 | 2600 | 20800
0
H/23 | Supply and install radial circuit for mechanical equipment (air conditioners etc) in 3x4.0 sq.mm SC PVC cables in conduit/ trunking complete with all accessories (allow radial length of 30m). | No. | 6 | 2600 | 15600
0
H/24 | Supply and install 20A single phasse isolators for abovemechanical equipment at locaations to be confirmed by the mechanical services sub-contractor. | No. | 6 | 1800 | 10800
H/25 | Supply and install radial circuit for mechanical equipment (air conditioners etc) in 5x4.0 sq.mm SC PVC cables in conduit/ trunking complete with all accessories (provisional, allow radial length of 30m). | No. | 3 | 3500 | 10500
0
H/26 | Supply and install 20A three phasse isolators for abovemechanical equipment at locaations to be confirmed by the mechanical services sub-contractor. | No. | 3 | 2500 | 7500
H/27 | Siingle blanking plates for future accessories for power, IT etc. | No. | 15 | 50 | 750
0
H/28 | Supply, install and connect telephone outlet box as per specifications | No. | 30 | 305 | 9150
E/29 | Supply, install and connect telephone outlet point consisting of average 15 meters of 25 mm diameter concealed heavy gauge PVC conduit inclusive of conduit, couplers, draw boxes, switch boxes, draw wire and other necessary accessories to the specialist's requirement complete with white blanking cover. | No. | 15 | 900 | 13500
0
| SUB-TOTAL CARRIED FORWARD TO NEXT PAGE |  |  |  | 1712400
| Brought Forward |  |  |  | 1712400
E/30 | Supply, install and connect data outlet point consisting of average 15 meters of 25 mm diameter concealed heavy gauge PVC conduit inclusive of conduit, couplers, draw boxes, switch boxes, draw wire and other necessary accessories to the specialist's requirement complete with white blanking cover. | No. | 15 | 900 | 13500
E/31 | Supply, install and connect CCTV, PIR sensor, vibration sensor, security outlet point consisting of average 15 meters of 20 mm diameter concealed heavy gauge PVC conduit inclusive of conduit, couplers, draw boxes, switch boxes, draw wire and other necessary accessories and white blanking cover to security alarm specialists requirements. (Provisional). | No. | 8 | 800 | 6400
E/32 | Supply, install and connect speaker/ public address outlet point consisting of average 15 meters of 20 mm diameter concealed heavy gauge PVC conduit inclusive of conduit, couplers, draw boxes, switch boxes, draw wire and other necessary accessories and white blanking cover to security alarm specialists requirements. (Provisional). | No. | 8 | 800 | 6400
E/33 | Supply and install CCTV outlet point complete with conduit, radial wiring in 2.5 sq. mm SC PVC cables and all accessories necessary and to the approval of the specialist sub-contractor. | No. | 8 | 1900 | 15200
E/34 | Allow for a provisional sum of 400,000.00 for additional specialized lighting (LEDs, architectural fittings etc) to latter instructions or omission. | Item | 1 | 400000 | 400000
H/35 | Supply and install PIR motion sensors units for lighting controls in toilets, passages and enclosed offices/ meeting rooms wired through contactors in 3x1.5 sq mm PVC single core cables complete with all accessories. | No. | 12 | 1400 | 16800
0
| SUB-TOTAL CARRIED FORWARD TO NEXT PAGE |  |  |  | 2170700
| Brought Forward |  |  |  | 2170700
H/36 | Supply and install PIR motion sensors with dual element infra red sensor, adjustable delay time and range of upto 6 meters. | No. | 12 | 11000 | 132000
H/37 | Supply and install 20A four pole contactors in ventillated metal enclosures for above circiuts. | No. | 4 | 7500 | 30000
H/38 | Allow for wiring to override backup switches in 3x1.5 sq mm PVC single core cables in concealed conduits. | No. | 4 | 1400 | 5600
H/39 | Supply and instal override backup switches. | No. | 4 | 1200 | 4800
0
H/40 | Allow for testing and commissioning of the entire electrical installation on this floor | Sum | 1 | 10000 | 10000
| SUB-TOTAL CARRIED FORWARD TO SUMMARY PAGE |  |  |  | 2353100

## Sheet1 (hidden)
Power supply for URINAL SENSORS, WATER TAP SENSORS, INSTANT SHOWERS | No. | 1950 | 0
1200mm green colour flourescent tubes. | No. | 750 | 0

## Sheet2 (hidden)
Ground floor | First floor | Second floor | Third floor | Fourth floor | Fifth floor
workstation 3...............9 | PASSIVE INFRA-RED................1 | LED Square Downlighter...........22 | FHR..............................2 | FHR..............................2 | LED Square Downlighter......13
LED Square Downlighter......18 | LED Square Downlighter...........23 | A1...............................189 | TV OUTLET........................1 | asst manager desk................11 | SWITCH......................7
A1..........................98 | TV OUTLET........................1 | TV OUTLET........................1 | workstation 2....................25 | d1000............................16 | COOKER......................1
workstation 2...............10 | workstation 2....................16 | workstation 2....................30 | workstation 3....................4 | TV OUTLET........................2 | workstation 3...............5
workstation 1...............22 | workstation 1....................31 | workstation 1....................17 | workstation 1....................22 | workstation 3....................3 | TV OUTLET...................4
SWITCH......................9 | workstation 3....................4 | workstation 3....................4 | PASSIVE INFRA-RED................1 | workstation 1....................34 | workstation 1...............17
TV OUTLET...................2 | A1...............................166 | MJ-SPUR..........................1 | LED Square Downlighter...........22 | workstation 2....................22 | workstation 2...............5
LGHT........................166 | MJ-SPUR..........................1 | Speaker..........................12 | A1...............................175 | PASSIVE INFRA-RED................1 | A1..........................86
Smoke Detector..............39 | Speaker..........................13 | 13A twin.........................72 | MJ-SPUR..........................1 | LED Square Downlighter...........42 | Heat Detector...............1
Speaker.....................13 | 13A twin.........................58 | LGHT.............................82 | 13A twin.........................65 | A1...............................153 | MJ-SPUR.....................2
13A twin....................46 | LGHT.............................95 | SWITCH...........................13 | Speaker..........................12 | MJ-SPUR..........................1 | 13A twin....................54
ACCESS CONTROL POINT........1 | SWITCH...........................12 | Smoke Detector...................45 | SWITCH...........................11 | LGHT.............................102 | Smoke Detector..............25
| Smoke Detector...................45 |  | Smoke Detector...................44 | 13A twin.........................65 | Speaker.....................9
|  |  | LGHT.............................85 | Smoke Detector...................37 | LGHT........................91
Speaker..........................15