## ELECTRICAL & FA BOQ
PROPOSED SERVICED APARTMENTS
AT
KESRA MOMBASA CAMPUS, MOMBASA COUNTY
FOR
M/S KENYA REVENUE AUTHORITY (Kenya School of Revenue Administration)
(ALL RATES TO BE INCLUSIVE OF 16% V.A.T AS APPLICABLE)
ELECTRICAL AND IT SERVICES INSTALLATIONS.
BILLS of QUANTITIES
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT (K.SHs)
P.00 | GENERAL ITEMS
A | Allow for the preparation of 'Shop' drawings in A1 size print to be displayed for the entirety of the project works. | Sum | 1 |  | 0
0
B | Allow for the preparation of all "As Built" Drawings and handover documentation including manuals, warranties and test results compilation. The tests shall be carried out as per the schedules attached with this bills of quantities document. All documents shall be submitted in triplicate hard copies, bound. Soft copies shall be presented in a CD ROM. All drawings shall be at 1:50 scale. | Sum | 1 |  | 0
| TOTAL CARRIED TO SUMMARY PAGE. |  |  |  | 0
ITEM | DESCRIPTION | UNIT. | QTY. | RATE. | AMOUNT in KSHS.
ELECTRICAL DISTRIBUTION SYSTEM INSTALLATIONS
E1.01.00 | Supply and deliver to site fittings, equipment and materials for Distribution System. Allow for storage on site all materials, fittings and equipment as stated below. Install, connect up-up complete including all conduits, supports, fixings, sleeves and accessories required for distribution system. Include for earthing requirements and connections and other item not detailed but required for the satisfactory completion and operation of the installation. The reference standard shall be the latest edition of the IET Wiring Regulations BS 7671.
Note:
The proposed equipment, fittings and cable manufacturers MUST be brands with more than 10 Years in the Kenyan market. The brand(s) specified for any fitting in this document should be understood to serve only as a quality reference guide.
Datasheets for all power distribution boards and cables shall be submitted with the bid and shall also be subject to inspection and approval by the Engineer before installation.
Circuit breaker coordination and selectivity requirements shall be determined on site.
Supply, Install, Test and Commission the following:
E1.01.01 | 3 x 10 sq.mm PVC/SWA insulated copper cable inclusive of all cable lugs, glands and shrouds, laid in 32mm dia. heavy gauge PVC conduits, from the Ground Floor Wall Mounted Electrical Meter Boards provided per block to the 18 No. Wing Consumer Units for all 3 No. Blocks (Provisional) | Lm | 240 |  | 0
E1.01.02 | Recess mount 15 Way Single Phase Power Consumer Unit in "Silverish Grey" finish. See "Schneider" Acti9 as reference. The CU shall be fitted complete with a 80A double pole MCB as Main Breaker. Allow in the rates for neatly printed circuit labelling in the C.U. Include in the rates for earthing of the power board to IEE regulations and to the satisfaction of the engineer (Wing Consumer Unit) | No. | 18 |  | 0
E1.01.03 | 80A DP RCCB (100mA Sensitivity) - Mounted in CU | No | 18 |  | 0
E1.01.04 | Type 1+2 240V, 50Hz, 3 Phase - 4 Pole ( 3P + N) AC Power Surge Protective Device rated for 12.5kA (L-L, L-N)/50kA (N-PE) Impulse Current (IImp), 1.5kV (Up), complete with temporary overvoltage withstand capability (for installation in the Main Meter Board provided per Block). | No. | 3 |  | 0
| TOTAL CARRIED FORWARD |  |  |  | 0
ITEM | DESCRIPTION | UNIT. | QTY. | RATE. | AMOUNT in KSHS.
| TOTAL BROUGHT FORWARD |  |  |  | 0
E1.01.05 | Allow a SUM of KES 35,000.00 per Meter Board for the Servicing and Repair of existing Meter Boards to comply with the minimum required standards for low voltage (415V) switchgear and control gear assemblies as specified in IEC 61439, including but not limited to suitability for external influences (IP rating), safe cable management and adequate protection against involuntary contact (protection against electric shock), proper warning labelling, proper circuit labelling within the board, safe means of isolation, protection against fault currents etc. | No. | 3 |  | 0
E1.01.06 | MCBs in the above consumer units;
a | 10A SP | No. | 54 |  | 0
b | 20A SP | No. | 72 |  | 0
c | 32A SP | No. | 72 |  | 0
d | Blanking plates for all spare ways. | No. | 18 |  | 0
E1.01.07 | 200mm (Width) X 50mm (Depth) double compartment heavy duty PVC cable trunking complete with cover, all cable retainers and mounting accessories as required (Provisional for Cable and Refrigerant Piping Management between Indoor AC Unit and Outdoor Unit) | Lm | 270 |  | 0
| TOTAL CARRIED TO SUMMARY PAGE. |  |  |  | 0
ITEM | DESCRIPTION | UNIT. | QTY. | RATE. | AMOUNT in KSHS.
POWER POINTS WIRING AND INSTALLATIONS
E1.02.00 | Supply and deliver to site materials, fittings and accessories, install, connect-up complete and commission the installation. Include in the rates for supply, installation and connecting up all cables including all required conduits, supports, fixings, sleeves and accessories for power point, install complete all conduits, supports, fixings, sleeves and accessories for voice and data points. Accessories manufacturers shall be of an approved quality, with the brands expected to have been in the Kenyan market for a period of at least 10 Years The reference standard for all small power installations shall be as the latest edition of the IET Wiring Regulations BS 7671.
Note! All fittings shall be subject to inspection and approval before installation.
E1.02.01 | 13 Amp Premium Quality Twin Socket Outlet Plates with USB charger in white finish. | No. | 48 |  | 0
E1.02.02 | Standard 13 Amp Premium Quality Twin Socket Outlet Plates in white surface finish. | No. | 204 |  | 0
E1.02.03 | 20 Amp Fused Spur Switch (For Fire Alarm Panel) | No. | 3 |  | 3
E1.02.04 | 20A DP Switch with Neon Indicator in grey finish | No. | 50 |  | 50
E1.02.05 | 32A DP Switch with Neon Indicator in white finish (For Solar Booster Elements and Water Pumps) | No. | 6 |  | 6
E1.02.06 | 1 Gang 45 Amps cooker control unit with neon indicator c/w 45 Amp cooker socket outlet in white surface finish. | No. | 18 |  | 18
E1.02.07 | Dual Voltage 115/230V Shaver Socket in polished chrome finish. | No. | 48 |  | 48
E1.02.08 | Dual Outlet TV/SAT Diplexer Outlet in white/grey finish | No. | 48 |  | 48
E1.02.09 | 32 Amps Rated IP67 SPN Rotary Isolator Switch and Face Plate c/w 3 Pin (1P+N+E) Industrial Socket Outlet and Plug for Pumps & AC Outdoor Equipment plugging. (Installations shall refer to the provided Electrical Schematic). | No. | 57 |  | 57
| TOTAL CARRIED FORWARD |  |  |  | 230
ITEM | DESCRIPTION | UNIT. | QTY. | RATE. | AMOUNT in KSHS.
| TOTAL BROUGHT FORWARD |  |  |  | 230
E1.02.10 | 13 Amps RING socket outlet points, wired at an average distance of 5 metres point to point, in 3 x 2.5mm2 PVC insulated and sheathed single core copper cables drawn in 20mm diameter heavy gauge PVC conduits concealed in walls and surface conduit installations within the ceiling void with all PVC conduit boxes and accessories but excluding the socket outlet face plates . | No. | 300 |  | 0
E1.02.11 | RADIAL Single Phase Isolator points wired, at an average approximate distance of 20 metres, in 3 x 4.0 mm2 PVC insulated and sheathed single core copper cables, drawn in 32mm diameter heavy gauge PVC conduits concealed in walls/floor/ceiling void with all PVC conduit boxes and accessories but excluding the Isolator. | No. | 57 |  | 0
E1.02.12 | DP Switch RADIAL outlet points, wired at an average approximate distance of 25 metres in 3 x 2.5 mm2 PVC insulated and sheathed single core copper cables drawn in 25mm diameter heavy gauge PVC conduits, concealed in walls/floor/ceiling void with all PVC conduit boxes and accessories but excluding the DP Switch. | No. | 53 |  | 0
E1.02.13 | DP Switch and Cooker Unit RADIAL outlet points, wired at an average approximate distance of 25 metres in 3 x 4.0 mm2 PVC insulated and sheathed single core copper cables drawn in 25mm diameter heavy gauge PVC conduits, concealed in walls/floor/ceiling void with all PVC conduit boxes and accessories but excluding the DP Switch. | No. | 24 |  | 0
E1.02.14 | Fire Alarm System Points in 25mm diameter heavy gauge PVC conduits concealed in walls and ceiling void, with all PVC conduit boxes and accessories, linking back to designated control/panel stations, but excluding all speakers, controllers and fittings. | No. | 75 |  | 0
E1.02.15 | Data System points in 25mm diameter heavy gauge PVC conduits concealed in walls and ceiling void, with all PVC conduit boxes and accessories, linking back to designated data cabinet positions, and inclusive of draw wires and blanking plates but excluding all Data fittings/equipment. | No. | 108 |  | 0
E1.02.16 | Flush wall mount Adaptor Box, 200mm x 200mm x 50mm, complete with cable entry knock outs and half thread bushes for interfacing electrical cable connections from floor to floor (Provisional). | No. | 30 |  | 0
| TOTAL CARRIED TO SUMMARY PAGE. |  |  |  | 230
ITEM | DESCRIPTION | UNIT. | QTY. | RATE. | AMOUNT in KSHS.
LIGHTING SYSTEM INSTALLATIONS
E1.03.00 | Supply and deliver to site all materials, fittings and accessories. Install, connect-up complete to IEE Regulatory requirements and Electrical Codes of Practice, test and commission the installations. Include in the rates for Supply, installation and connecting complete all cables including all required conduits, supports, fixings, sleeves and accessories.
The recommended light fittings and accessories manufacturers shall be brands that have been in the market for more than 10 Years. Any brands indicated here shall serve only as a quality reference.
The final decision and approval of color temperatures shall be done on site.
All light fittings shall be subject to approval by the Architect and Engineer.
Special note shall be taken to ensure that:-
i) Earth conductors are drawn and terminated to all lighting switch boxes
ii) Lighting fittings to be supplied complete with lamps, fixings brackets and accessories.
Supply and Install the following:
Conduits and Wiring
E1.03.01 | Lighting system points wired in 3 x1.5mm2 PVC insulated and sheathed single core copper cables, drawn in 20mm diameter heavy gauge PVC conduits concealed in walls/within the ceiling voids, with links to the raw power consumer unit inclusive of all PVC conduit boxes and accessories but excluding switch and light fittings. | No. | 346 |  | 0
Light Fittings and Accessories
E1.03.02 | Allow a SUM of KES 10,000 for the guest room decorative ceiling fitting | No. | 48 |  | 0
E1.03.03 | Ball Fitting for guest washrooms c/w 7W LED Frosted Bulb | No. | 48 |  | 0
E1.03.04 | 12W 280mm diameter 3000K Crown Ceiling Light fitting (See Light Green Code No. LG-PRL12W-3K for reference) - For Internal Corridors and Kitchen | No. | 36 |  | 0
E1.03.05 | ditto but in Mushroom Type and 6000K Color Temperature - For Stairway | No. | 9 |  | 0
E1.03.06 | 8W 180mm diameter 3000K Ceiling Light fitting (See Light Green Code No. LG-PRL8W-3K for reference) - For Balconies + Under Stairs | No. | 39 |  | 0
E1.03.07 | Decorative IP65 rated LED outdoor security light fitting in black anodized finish | No. | 18 |  | 0
E1.03.08 | 50W flood light fitting | No. | 4 |  | 0
| TOTAL CARRIED TO SUMMARY PAGE. |  |  |  | 0
ITEM | DESCRIPTION | UNIT. | QTY. | RATE. | AMOUNT in KSHS.
LIGHTING SYSTEM INSTALLATIONS continued…
| TOTAL BROUGHT FORWARD |  |  |  | 0
E1.03.09 | Bathroom Mirror Light in white finish | No. | 48 |  | 0
E1.03.10 | IP66 rated in wall 3W LED Step Lights (For use as guest room night lights) | No. | 96 |  | 0
Switches and Controls:
E1.03.29 | Premium quality 2 Gang 2 Way Switch in white surface finish. | No. | 108 |  | 0
E1.03.30 | Premium quality 1 Gang 2 Way Switch in white surface finish. | No. | 36 |  | 0
E1.03.31 | Premium quality 1 Gang 1 Way Switch in white surface finish. | No. | 126 |  | 0
| TOTAL CARRIED TO SUMMARY PAGE. |  |  |  | 0
ITEM | DESCRIPTION | UNIT. | QTY. | RATE. | AMOUNT in KSHS.
FIRE ALARM SYSTEM INSTALLATIONS
E1.04.00 | Supply and deliver on site materials, equipment and accessories complete. Install, connect -up complete IEE Regulatory requirements and Electrical codes of Practice and commission the installation. Include in the rates for supply of all materials and connect- up complete in FIRE TUFF cables including all conduits, supports, fixings, sleeves and accessories required for fire alarm and detection system all linked to the Fire Alarm Panel. Allow for testing and commissioning of the complete fire alarm system installations and include for any other item not specifically detailed but required for the satisfactory installation and operation of the system.
E1.04.01 | Conventional Fire Alarm Control Panel complete with 72 Hour standby battery with integral charger and mains input of 240V A/C and 24V DC operating voltage. The panel shall support a minimum of 40 devices and 2 Zones. | No. | 3 |  | 0
E1.04.02 | Smoke detector points wired in 1.5mm2 FIRE TUFF single core copper cables drawn in 25mm diameter heavy gauge conduits concealed in walls and surface conduits installations within the ceiling void with PVC conduits boxes and accessories with links to the ground floor fire alarm panel and excluding break glass - wiring to be done in accordance with zoning requirements. | No. | 90 |  | 0
E1.04.03 | Ditto but for Manual Call Points. | No. | 18 |  | 0
E1.04.04 | Fire alarm Sounder points wired in 2.5 mm2 FIRE TUFF single core copper cables ditto. | No. | 18 |  | 0
E1.04.05 | Conventional fire alarm manual call point as MENVIER MBG914 accessorized with mounting Bezels for MBG Call points as MBGBEZ and MBGHinged Cover as MBGHCC. | No. | 18 |  | 0
E1.04.06 | Conventional fire alarm Sounder/Beacon with shallow base-Red as MENVIER MCD524/SB. | No. | 18 |  | 0
E1.04.07 | Conventional Photo-thermal Smoke detector complete with base as MENVIER MPT951. | No. | 90 |  | 0
E1.04.05 | Allow a sum for integration of the newly installed fire alarm system into the existing institution's fire alarm system, configuration and for testing and commissioning of the fire alarm system. | No. | 1 |  | 0
| TOTAL CARRIED TO SUMMARY PAGE. |  |  |  | 0
ITEM | DESCRIPTION | UNIT. | QTY. | RATE in KShs. | AMOUNT in KShs.
STREET/EXTERNAL LIGHTING AND LIGHTNING SYSTEM INSTALLATIONS
E1.05.00 | Supply and deliver to site materials, fittings and accessories, install, connect-up complete to IEC Regulatory requirements and Electrical Codes of Practice, test and commission the installation. Include in the rates for Supply, installation and connecting-up all cables including all required conduits, supports, fixings, sleeves and accessories for lighting point. Cabling materials and lighting fittings manufacture shall be fully compliant to ISO/IEC/IEEE requirements and approved.
The light fittings, lighting controls and accessories manufacturers MUST be brands with more than 10 Years in the lighting market. The brand(s) specified for any fitting in this document should be understood to serve only as a quality reference guide. All LED fittings MUST have a minimum warranty of 2 Years and a guarantee of at least 30,000 hours. Light fittings shall be supplied inclusive of all accessories and lamps, and shall be subject to review and approval by the engineer.
Supply, Install, Test and Commission the following:
E1.05.01 | 3 Core 10 sq.mm XLPE/SWA copper cable, inclusive of all cable lugs, glands and shrouds, laid in 38mm diameter heavy gauge PVC duct in ground from the nearest LV Distribution Board to the Road Lighting Pillar (Provisional) | Lm | 20 |  | 0
E1.05.02 | Pole Points wired in 3 Core x 10 sq.mm XLPE/SWA insulated copper cable, drawn in 32mm diameter heavy gauge PVC conduits concealed in ground, complete with cable glands and lugs, with links to the Road Lighting Pillar (Provisional) | Lm | 100 |  | 0
E1.05.03 | 5M Q235 Mild Steel, Hot Dip Galvanized, powder coated Single Arm Street Light Pole complete with appropriately sized base plates and foundation bolts. Include in the rates for a loop in-loop out box/adaptor box complete with knock-outs, connectors and fuse, and the construction of a concrete base with provision for maintenance access for each street light pole. | No. | 4 |  | 0
E1.05.04 | IP66 99W LED Flood Lamp/Light fitting for the Street Light Poles as "Italo" Street Ref No. IT2-SO5-4.7-5M1F or a variant of similar design and quality. | No. | 4 |  | 0
E1.05.05 | IP66 rated Lockable Standard Feeder/Control pillar complete with DIN rail to house street lighting control gear. | No. | 1 |  | 0
E1.05.06 | Street Lighting Photocell with a 1000W LED capacity. See "Lucy Zodion" SS5 Series Street Lighting Photocell (SS5DR/HD). | No. | 1 |  | 0
| TOTAL CARRIED FORWARD |  |  |  | 0
ITEM | DESCRIPTION | UNIT. | QTY. | RATE. | AMOUNT in KSHS.
| TOTAL BROUGHT FORWARD |  |  |  | 0
E1.05.07 | PME earthing on every third street light pole comprising 25mm Diameter x 1500mm Long Steel core copper clad earth electrode, 6 sq. mm earth lead, earth clamp and complete with all accessories. | Item | 2 |  | 0
E1.05.08 | 20A SP/N Contactor | No. | 1 |  | 0
E1.05.09 | 2.5 sq.mm 3 Core PVC/PVC insulated copper cable from photocell to 20A SP/N contactor | Lm | 10 |  | 0
E1.05.10 | 2.5 sq.mm 3 Core PVC/PVC insulated copper cable from Pole Connectors to Lamps | Lm | 20 |  | 0
E1.05.11 | 20A MCBs in Control/Feeder Pillars | No. | 2 |  | 0
E1.05.12 | 2-Pole Single Phase 12.5kA SPD for protection of the Control Pillar Circuits. | No. | 1 |  | 0
E1.05.13 | Allow a rate for trenching and backfilling, and the provision of "HATARI" labelled tiles | Lm | 100 |  | 0
Lightning Arresting System
E1.05.14 | 25mm x 2mm copper conductor tape as 'FURSE' Cat. No.TAO30 OR Equivalent, complete with copper saddles, fixings, etc. 38mm pvc conduit drop to earth rods at ground level. | Lm | 45 |  | 0
E1.05.15 | Lightning arrestors with 1300mm x 20mm diameter rod complete with 800mm long multiple point top as FURSE' Cat. No. RA555/RA610 OR Equivalent. | No. | 3 |  | 0
E1.05.16 | Flat saddles for supporting 20mm diameter lighting arrestors as 'FURSE' Cat. No. SD130 OR Equivalent | No. | 6 |  | 0
E1.05.17 | 16mm diameter x 1200mm long stainless steel core copper earth rod on 'FURSE' Cat. No. RS005. | No. | 3 |  | 0
E1.05.18 | Screw down type test clamps, suitable for 25mm tape as FURSE' Cat. No. CT305 OR Equivalent. | No. | 3 |  | 0
E1.05.19 | 70mm2 SC PVC/SWA/PVC copper (Cu) cable for earthing interlink to all lightning protection earth drop points around the buildings. | Lm | 40 |  | 0
E1.05.20 | Allow for testing the complete lightning protection system as per the specification including any additional material required. | Item | 1 |  | 0
| TOTAL CARRIED TO SUMMARY PAGE. |  |  |  | 0
KESRA MOMBASA GUEST APARTMENTS/HOTEL - ELECTRICAL AND FIRE ALARM INSTALLATIONS - SUMMARY PAGE.
ITEM | DESCRIPTION |  |  | AMOUNT (IN KSHS)
P.00 | GENERAL ITEMS |  |  | 0
E1.01.00 | ELECTRICAL DISTRIBUTION SYSTEM INSTALLATIONS |  |  | 0
E1.02.00 | POWER POINTS WIRING AND INSTALLATIONS |  |  | 230
E1.03.00 | LIGHTING SYSTEM INSTALLATIONS |  |  | 0
E1.04.00 | FIRE ALARM SYSTEM INSTALLATIONS |  |  | 0
E1.05.00 | STREET/EXTERNAL LIGHTING AND LIGHTNING SYSTEM INSTALLATIONS |  |  | 0
| TOTAL FOR ELECTRICAL & IT SERVICES INSTALLATIONS CARRIED TO MAIN COLLECTION PAGE |  |  | 230